## Slide 1: YORK机组常见启动柜介绍
  1. 直接启动式启动器
  2. 星-三角转换启动器
  3. 固态启动器（SSS）
  4. 可变速启动器（VSD）
  资料来源：httpwww.sjzmidea.com.cn/

## Slide 2: 约克中央空调主要启动方式
1/星－三角启动器方式
结构简单、可靠，
启动电流200-300%FLA，有两次的电流冲击。
2/固态启动器方式（利用可控硅控制降压启动）
外形小,可挂在电机旁边，
启动电流300-400%FLA，有一次的电流冲击。
3/ VSD变频器启动方式
启动电流不会超过100%FLA（满载电流）

## Slide 3: 电流--时间图

## Slide 5: 星－三角启动和VSD启动曲线

## Slide 6: 星三角启动器

## Slide 7: 控制主板

## Slide 8: 主板跳线说明
JP52－IN:英制单位：
OUT:公制单位
JP51－IN:无30分钟延时
OUT:有30分钟延时

## Slide 9: VSD变频器图

## Slide 10: 约克MillenniumTM 离心机组变频调速装置
最佳节能调节控制方式

## Slide 11: 讨论专题
什么是变速驱动装置
变频调速离心机组的优越性能
机组部分负荷运行性能的重要性
约克变频装置的广泛应用和成功经验
小结
Notes: Here are the list of topics that are covered in this presentation.

## Slide 12: 讨论专题
什么是变速驱动装置
Notes: Here are the list of topics that are covered in this presentation.

## Slide 13: 变频调速装置
VSD--Variable Speed Drive
应用广泛
  空气处理箱
  水泵
  冷却塔
  离心冷水机组
Notes: You may be familiar with other types of inverters. Many people use them on air handling units, pumps, cooling tower motors and even centrifugal chillers. Some chiller manufacturers rely on general purpose VSD抯 for use on their centrifugal chillers. York抯 VSD is different. The Millennium VSD was designed by York engineers specifically for centrifugal chillers. The Millennium VSD utilizes Adaptive Capacity Control Logic, which optimizes the prerotation vane position and motor speed to minimize energy consumption. This patented technology is only offered by York.

## Slide 14: 讨论专题
什么是变速驱动装置
变频调速离心机组的优越性能
Notes: Here are the list of topics that are covered in this presentation.

## Slide 15: 约克MILLENNIUM 变速驱动
1524mm
1372mm
457mm
专为冷水机组设计
具有最佳控制逻辑
直接安装在机组上
结构紧凑尺寸小
工厂完成安装接线 与调试
整机 UL认证
最小频率可调节至 30HZ

## Slide 16
MillenniumTM
离心式冷水机组
VSD直接安装
在机组上

## Slide 17: 采用变频装置机组的优越性
节约能耗
安全运行
宁静运转
低电流启动
减少维修与维护
Notes: Here are some of the features and benefits of the Millennium Variable Speed Drive.

## Slide 18: 采用变频装置机组的优越性
节约能耗
安全运行
宁静运转
低电流启动
减少维修与维护
Notes: Here are some of the features and benefits of the Millennium Variable Speed Drive.

## Slide 19: 工作原理
优化电机转速
优化导流叶片的开度
冷冻水温度
温度设定值
蒸发/冷凝压力
导流叶片开度
电机实际转速
随时监测冷冻水温度等工作状态
参数，根据冷量需求同时调节电
机转速和导流叶片开度，优化机
组部分负荷性能，节省运行费用
。

## Slide 20: 控制性能是节能的关键因素
精确反映机组的运行参数
避开机组运行的喘振点
调节转速，优化效率
Notes: Control of the VSD / chiller package is the key to energy savings. Slight differences in impeller geometry makes each compressor unique. The chiller operating conditions are also unique. York抯 Adaptive Capacity Control logic actually 搇earns?how the chiller operates, mapping exact surge points. It may take an entire cooling season to completely map the system. This allows operation near the surge points to minimized speed for peak efficiency.

## Slide 21: 离心式机组组件示意图
Notes: Let抯 take a look at how the motor and prerotation vanes fit into the chiller system.

## Slide 22: 组件
蒸发器
冷凝器
电机
齿轮
叶轮
导流叶片
Notes: Here are the major components of a centrifugal chiller. Let抯 begin in the evaporator shell. Liquid refrigerant boils in the evaporator and becomes refrigerant vapor. This vapor then passes through the prerotation vanes. The motor turns the impeller using shafts and gears. The refrigerant vapor then enters the 揺ye?of the impeller. As the impeller rotates, the refrigerant is compressed and discharged into the condenser.

## Slide 23: 恒速 变速
负荷下降时：
导流叶片关闭
电机转速恒定
Notes: As the load on the chiller decreases, the prerotation vanes begin to close. The closing of the vanes restricts the amount of refrigerant allowed into the eye of the impeller, thus reducing the cooling effect. Notice that the motor continues to operate a the same speed regardless of the load.

## Slide 24: 恒速 变速
负荷下降时：
专为冷水机组的独特控制逻辑
电机转速减慢
优化导流叶片的开度
压缩机保持高效
节省运行费用
负荷下降时：
导流叶片关闭
电机转速恒定

## Slide 25: YORK MILLENNIUM 变速驱动装置( VSD)
电脑板上显示信息包括：
  电压，电流，频率，功率，电能耗
  输入功率
  总的功率因数
  3相电压总的谐波失真
  3相电流总的谐波失真
  自诊断检修参数

## Slide 26: Millennium变频驱动装置可大大优化机组部分负荷时的性能
Notes: The Millennium VSD optimizes off-design performance.

## Slide 27: 讨论专题
什么是变速驱动装置
变频调速离心机组的优越性能
机组部分负荷运行性能的重要性
Notes: Here are the list of topics that are covered in this presentation.

## Slide 28: 机组平均大约 99%的时间下运行在部分负荷工况，因而部分负荷情况的能耗是评价机组性能的重要标志.
Notes: Nearly, 99% of all chiller run hours are at off-design conditions. Let抯 take a look at some actual weather data.

## Slide 29: 广州地区天气情况
99.5%
室外环境温度（ºF）
冷却水温度（ºF）
年统计小时数

## Slide 30: MILLENNIUM离心机 -变速驱动与恒速驱动机组的比较

## Slide 31
YORK恒速机组
60% 负荷
100% 负荷
80% 负荷
其他厂家r
60% 负荷
100% 负荷
80% 负荷
YORK 变速驱动
100% 负荷
80% 负荷
60% 负荷
冷冻水进水温度

## Slide 32: 变速驱动离心机
年运行费用节省30%
负荷%
kW/Ton

## Slide 33: MILLENNIUM离心机
年平均运行费用节省25 - 30%
选配新型变速驱动装置，直接安装在机组上，无需
另占机房面积，大大改善机组部分负荷性能。

## Slide 34: 采用变频装置机组的优越性
节约能耗
安全运行
宁静运转
低电流启动
减少维修与维护
Notes: Here are some of the features and benefits of the Millennium Variable Speed Drive.

## Slide 35: 采用变频装置机组的优越性
节约能耗
安全运行
宁静运转
低电流启动
减少维修与维护
Notes: Here are some of the features and benefits of the Millennium Variable Speed Drive.

## Slide 36: 采用变频装置机组的优越性
节约能耗
安全运行
宁静运转
低电流启动
减少维修与维护
Notes: Here are some of the features and benefits of the Millennium Variable Speed Drive.

## Slide 37
约克VSD优化机组启动性能
0
5
10
15
20
30
40
100%
200%
300%
400%
500%
时间（秒）
电机FLA （%）
Millennium VSD
星三角启动器
机组启动电流决不超
过电机的满负荷电流

## Slide 38: 采用变频装置机组的优越性
节约能耗
安全运行
宁静运转
低电流启动
减少维修与维护
Notes: Here are some of the features and benefits of the Millennium Variable Speed Drive.

## Slide 39: 冷量范围（50HZ）
150 tons
1100 tons
Notes: York currently offers the Millennium VSD for centrifugals that fall between approximately 150 and 650 tons.
Note: Millennium VSD will be offered at higher tonnages in the future.

## Slide 40: 适用于各种冷媒之 离心机组
R - 22
R - 134a
R - 123
Notes: The Millennium VSD is applicable with R-123, R-22 and R-134a.
Note: The Millennium VSD is also available with R-11. However, this may entice the customer to prolong retrofitting of replacing their R-11 chiller. The customer may opt for a Millennium VSD without addressing CFCs.

## Slide 41: 工程应用
于1979年第一台装置投入运行
至今已有近二十年实践经验
1500 个以上的安装工程实例
平均二至三年收回投资
既可在安装在新制机组上也可在已有离心机组上改装

## Slide 42: 小结
独特控制逻辑，优化部分负荷性能
节能!
优化机组启动性能，减少磨损
延长设备寿命
低负荷低转速运行
运行宁静
自1979年起，超过1500个工程
本行业最富经验

## Slide 43: VSD变频器介绍
1/ 电机软启动
启动电流不超过100%FLA。减少驱动装置的冲击和磨损。
2/ 节能运行
节约用户大量的运行费用，一般地20-30%
3/ 增强机组的卸载能力
可以克服离心机在低负荷运行产生的“喘振”，可以满足离心机在低负荷下运行，扩大使用范围。
4/ 运行宁静
机组运行安静、平稳，延常使用寿命。
5/ 修正功率因素
能够自动将功率因素修正至0.95甚至更高。

## Slide 44: VSD变频器原理
*原理介绍：
变频器： AC-DC-AC
*根据下列因素实现进行最优控制
1/冷冻水出水温度
2/冷冻水设定值
3/压缩机的压头（冷凝压力－蒸发压力）
4/导叶的开度
5/电机的频率

## Slide 45: 广州使用变频器的用户
    广州百货大厦，YT机组 加变频器
    广州火车东站综合楼，YK机组
    广东省检验检疫局，YK机组 加变频器
    广州市检察院，YK机组
    广州宝洁公司纸品厂 二台YK机组
    广州邮电大楼 YK机组
    广州新体育馆 YK机组
    广州万国广场 YK机组
    新机场飞机维修公司 二台YK机组
    广州公安局 YT机组
    好又多芳村分店 YK机组